## C2 Form
BOILER TUBE FAILURE REPORT (C-2 FORM)
(C-2 FORM SHOULD BE SENT WITHIN 12 HOURS OF SYNCHRONISATION)
1) STATION: | NTPL | 2) UNIT No. |  | I | 3) LAST UNIT OUTAGE |  |  | 2018-10-01 | 4) LAST UNIT O/H |  | 2017-06-01
5) UNIT SHUTDOWN FROM |  | 30 | 11 | 18 |  | 12 | 30 | 9) OUTAGE HOURS |  | 28 | 05
6) WATER FILLING CLEARANCE |  | 01 | 12 | 18 |  | 13 | 25 | (ONLY DUE TO BTF) |  | hh | mm
7) CLEARANCE FOR LIGHTUP |  | 01 | 12 | 18 |  | 16 | 35 | 10) GENERATION LOSS |  | 16.2
(AFTER REPAIR OF BTF) |  | dd | mm | yy |  | hh | mm | (ONLY DUE TO BTF) |  | MUS
8) UNIT SYNCHRONISED AT |  | 1 | 12 | 18 |  | 20 | 54
11) BTF INSPECTED BY |  | dd | mm | yy |  | hh | mm
| BTF COMMITTEE HEAD |  |  |  |  | MTP |  |  |  | FQA
|  | CHEMISTRY |  |  |  | OPERATION |  |  |  | O&C
BOILER TUBE FAILURE LOCATION
12) FAILED TUBE LOCATION MARKED ON UNIT MATERIAL DIAGRAM AND BOILER GENERAL ARRANGEMENT DRAWING
(CLEARLY IDENTIFYING TUBE NO., COIL NO., TUBE DIMENSION, TUBE MATERIAL AND X,Y,Z COORDINATES)
Tube Dimension - D51 x 5 mm; Tube Material - SA 210 Gr. C; Tube Number - 37 & 38 from LHS water wall in front water wall at 51 Mtr level
DESCRIPTION OF BOILER FAILED TUBES
13) PHOTOGRAPHS OF LOCATION OF FAILURE BEFORE START OF REPAIR WORK
Same as below
14) PHOTOGRAPHS OF PRIMARY FAILED TUBE
15) PHOTOGRAPHS OF REPAIRED LOCATION AFTER RESTORATION WORK
Not Available
16) DETAILS OF REPAIR WORK (SPECIFY JOINT DETAILS, COIL NO./ TUBE NO. & RESTORATION WORK)
AT 51 Mtr Elevation
1 | Erection attachment fin weld failure in front water wall of Tube 37 & 38 from LHS water wall. Metal build up - Tube number 39
NO.OF JOINTS - 4 erection welds + 1 weld build up
17) DETAILS OF INSPECTION OF ADJACENT AND IDENTICAL LOCATIONS
Thickness survey carried out for adjacent tubes for any steam erosion
18) HISTORY OF WORK IN FAILED TUBE/COIL/LOCATION IN PAST FIVE YEARS
YEAR | HISTORY OF WORK (DETAILS OF WORK DONE IN THE AREA/COIL
| LOCATION | Tube/Coil No. |  |  | No. OF TUBES REPLACED |  |  | NATURE OF FAILURE & WORK
NIL
19) STATION OBSERVATION W.R.T. CAUSE OF TUBE FAILURE
Root Cause - Erection attachment fin weld failure
COPY TO: |  | 1) DISPLAY IN UCB
2) GM/O&M
3) HOD (OS-BOILER)
(SIGNATURE OF BTF HEAD)
NAME:
DESIGNATION:
DATE: