## SAMPLE
BOILER TUBE FAILURE REPORT (C-2 FORM)
(C-2 FORM SHOULD BE SENT WITHIN 12 HOURS OF SYNCHRONISATION)
1) STATION: | NTPL | 2) UNIT No. |  | II | 3) LAST UNIT OUTAGE |  |  |  | 4) LAST UNIT O/H |  | 2018-08-01
5) UNIT SHUTDOWN FROM |  | 20 | 09 | 18 |  | 11 | 45 | 9) OUTAGE HOURS
6) WATER FILLING CLEARANCE |  | 24 | 09 | 18 |  | 01 | 15 | (ONLY DUE TO BTF) |  | hh | mm
7) CLEARANCE FOR LIGHTUP |  | 24 | 09 | 18 |  | 08 | 35 | 10) GENERATION LOSS
(AFTER REPAIR OF BTF) |  | dd | mm | yy |  | hh | mm | (ONLY DUE TO BTF) |  | MUS
8) UNIT SYNCHRONISED AT |  | 24 | 9 | 18 |  | 14 | 25
11) BTF INSPECTED BY |  | dd | mm | yy |  | hh | mm
| BTF COMMITTEE HEAD |  |  |  |  | MTP |  |  |  | FQA
|  | CHEMISTRY |  |  |  | OPERATION |  |  |  | O&C
BOILER TUBE FAILURE LOCATION
12) FAILED TUBE LOCATION MARKED ON UNIT MATERIAL DIAGRAM AND BOILER GENERAL ARRANGEMENT DRAWING
(CLEARLY IDENTIFYING TUBE NO., COIL NO., TUBE DIMENSION, TUBE MATERIAL AND X,Y,Z COORDINATES)
DESCRIPTION OF BOILER FAILED TUBES
13) PHOTOGRAPHS OF LOCATION OF FAILURE BEFORE START OF REPAIR WORK
14) PHOTOGRAPHS OF PRIMARY FAILED TUBE
15) PHOTOGRAPHS OF REPAIRED LOCATION AFTER RESTORATION WORK
16) DETAILS OF REPAIR WORK (SPECIFY JOINT DETAILS, COIL NO./ TUBE NO. & RESTORATION WORK)
AT 19 ml
PRIMARY | S-Panel slope tube no: 1 from LHS WW - ERECTION JOINT FAIURE - spool piece added -2 joints
SECONDARY | S-Panel slope tube no: 2,3,4,5 from LHS WW- Steam erosion - spool piece added -8 joints
| LHS WW tube no : 211,212,213 |  | ,213 from Front wall - steam erosion -Spool piece added - 6 joints
AT 52 ml
SECONDARY | corner transition tube no :4 from LHS WW - fish mouth opening due to starvation due to punture at 19 ml - | [7 empty] | spool piece added- 2 joints
corner transition tube no :2,6 from LHS WW - steam erosion - spool piece added - 4 joints
corner transition tube no :3,5 from LHS WW - welding accesability - spool piece added - 4 joints
AT 60 ml
PRIMARY | rear arch goose nech slope between RH(F) and RH® TUBE NO 65,165 - ERECTION WELD FAILURE- spool piece added -4 joints
SECONDARY | rear arch goose nech slope between RH(F) and RH® TUBE NO 66,166 - STEAM EROSION - spool piece added -4 joints
AT 10 ml
PRIMARY | RHS WW Tube no 93,94 from front ww - ERECTION WELD FAILURE - spool piece added - 4 JOINTS
AT 54 ml
PRIMARY | Back pass front steam cooled wall tube no 4 from LHS - LONGITUTINAL CRACK in bucksty support attachement weld- spool piece added -2 joints
17) DETAILS OF INSPECTION OF ADJACENT AND IDENTICAL LOCATIONS
thickness survey carried out for adjacent tubes for any steam erosion
18) HISTORY OF WORK IN FAILED TUBE/COIL/LOCATION IN PAST FIVE YEARS
YEAR | HISTORY OF WORK (DETAILS OF WORK DONE IN THE AREA/COIL
| LOCATION | Tube/Coil No. |  | No. OF TUBES REPLACED |  |  |  | NATURE OF FAILURE & WORK
NIL
19) STATION OBSERVATION W.R.T. CAUSE OF TUBE FAILURE
COPY TO: |  | 1) DISPLAY IN UCB
2) GM/O&M
3) HOD (OS-BOILER)
(SIGNATURE OF BTF HEAD)
NAME:
DESIGNATION:
DATE: