## SAMPLE
BOILER TUBE FAILURE REPORT (C-2 FORM)
(C-2 FORM SHOULD BE SENT WITHIN 12 HOURS OF SYNCHRONISATION)
1) STATION: | NTPL | 2) UNIT No. |  | I | 3) LAST UNIT OUTAGE |  |  | 25.05.18 | 4) LAST UNIT O/H |  | 2018-04-01
5) UNIT SHUTDOWN FROM |  | 08 | 06 | 18 |  |  |  | 9) OUTAGE HOURS |  | 30 | 00
6) WATER FILLING CLEARANCE |  | 10 | 06 | 18 |  | 01 | 00 | (ONLY DUE TO BTF) |  | hh | mm
7) CLEARANCE FOR LIGHTUP |  | 10 | 06 | 18 |  |  |  | 10) GENERATION LOSS
(AFTER REPAIR OF BTF) |  | dd | mm | yy |  | hh | mm | (ONLY DUE TO BTF) |  | MUS
8) UNIT SYNCHRONISED AT
11) BTF INSPECTED BY |  | dd | mm | yy |  | hh | mm
| BTF COMMITTEE HEAD |  |  |  |  | MTP |  |  |  | FQA
|  | CHEMISTRY |  |  |  | OPERATION |  |  |  | O&C
BOILER TUBE FAILURE LOCATION
12) FAILED TUBE LOCATION MARKED ON UNIT MATERIAL DIAGRAM AND BOILER GENERAL ARRANGEMENT DRAWING
(CLEARLY IDENTIFYING TUBE NO., COIL NO., TUBE DIMENSION, TUBE MATERIAL AND X,Y,Z COORDINATES)
DESCRIPTION OF BOILER FAILED TUBES
13) PHOTOGRAPHS OF LOCATION OF FAILURE BEFORE START OF REPAIR WORK
14) PHOTOGRAPHS OF PRIMARY FAILED TUBE
15) PHOTOGRAPHS OF REPAIRED LOCATION AFTER RESTORATION WORK
16) DETAILS OF REPAIR WORK (SPECIFY JOINT DETAILS, COIL NO./ TUBE NO. & RESTORATION WORK)
Primary - Erection weld below economiser coil lower bank Coil 156 Row 2 (Spool Replacement)
Secondary - Steam erosion of adjacent tubes. Row 1 - Coil 154 & 155; Row 2 - Coil 154, 155 & 157; Row 3 - Coil 155, 156 & 157 (Spool replacement)
Preventive repair - Row 1 - Coil 158, 159; Row 2 - Coil 158, 159 (Joint)
17) DETAILS OF INSPECTION OF ADJACENT AND IDENTICAL LOCATIONS
Physical inspection of adjacent tubes to check for erosion.
18) HISTORY OF WORK IN FAILED TUBE/COIL/LOCATION IN PAST FIVE YEARS
YEAR | HISTORY OF WORK (DETAILS OF WORK DONE IN THE AREA/COIL
| LOCATION | Tube/Coil No. |  | No. OF TUBES REPLACED |  |  |  | NATURE OF FAILURE & WORK
NIL
19) STATION OBSERVATION W.R.T. CAUSE OF TUBE FAILURE
COPY TO: |  | 1) DISPLAY IN UCB
2) GM/O&M
3) HOD (OS-BOILER)
(SIGNATURE OF BTF HEAD)
NAME:
DESIGNATION:
DATE: