## C2 Form
BOILER TUBE FAILURE REPORT (C-2 FORM)
(C-2 FORM SHOULD BE SENT WITHIN 12 HOURS OF SYNCHRONISATION)
1) STATION: | NTPL | 2) UNIT No. |  | I | 3) LAST UNIT OUTAGE |  |  | 2020-07-01 | 4) LAST UNIT O/H |  | 2020-12-01
5) UNIT SHUTDOWN FROM |  | 15 | 05 | 21 |  | 18 | 56 | 9) OUTAGE HOURS |  | 33 | 15
6) WATER FILLING CLEARANCE |  | 16 | 05 | 21 |  | 23 | 00 | (ONLY DUE TO BTF) |  | hh | mm
7) CLEARANCE FOR LIGHTUP |  | 17 | 05 | 21 |  | 01 | 12 | 10) GENERATION LOSS
(AFTER REPAIR OF BTF) |  | dd | mm | yy |  | hh | mm | (ONLY DUE TO BTF) |  | MUS
8) UNIT SYNCHRONISED AT |  | 17 | 05 | 21 |  | 04 | 15
11) BTF INSPECTED BY |  | dd | mm | yy |  | hh | mm
| BTF COMMITTEE HEAD |  |  |  |  | MTP |  |  |  | FQA
|  | CHEMISTRY |  |  |  | OPERATION |  |  |  | O&C
BOILER TUBE FAILURE LOCATION
12) FAILED TUBE LOCATION MARKED ON UNIT MATERIAL DIAGRAM AND BOILER GENERAL ARRANGEMENT DRAWING
(CLEARLY IDENTIFYING TUBE NO., COIL NO., TUBE DIMENSION, TUBE MATERIAL AND X,Y,Z COORDINATES)
Tube dimension - 51x5 mm; SA 210 Gr.C . Corner 2 Corner Transistion tube number 25 @ 18 ML
DESCRIPTION OF BOILER FAILED TUBES
13) PHOTOGRAPHS OF LOCATION OF FAILURE BEFORE START OF REPAIR WORK
14) PHOTOGRAPHS OF PRIMARY FAILED TUBE
Primary Damage is underside of fin of the Corner Transition tube
15) PHOTOGRAPHS OF REPAIRED LOCATION AFTER RESTORATION WORK
16) DETAILS OF REPAIR WORK (SPECIFY JOINT DETAILS, COIL NO./ TUBE NO. & RESTORATION WORK)
S-Panel to Corner 2 Transition @ 18 ML
Erection/Shop attachment weld failure. Observed slight undercut in attachment welding
Attended as Pinhole
Secondary damage erosion observed in Rear Waterwall Tube 1 @ 18 ML.
Repair attended by Metal build up
17) DETAILS OF INSPECTION OF ADJACENT AND IDENTICAL LOCATIONS
Dye Penetrant Testing of adjacent areas of failure for confirmation of only defect. Physical inspection of any erosions. None Observed
18) HISTORY OF WORK IN FAILED TUBE/COIL/LOCATION IN PAST FIVE YEARS
YEAR | HISTORY OF WORK (DETAILS OF WORK DONE IN THE AREA/COIL
| LOCATION | Tube/Coil No. |  |  | No. OF TUBES REPLACED |  |  | NATURE OF FAILURE & WORK
NIL
19) REMARKS
20) STATION OBSERVATION W.R.T. CAUSE OF TUBE FAILURE
Erection/Shop attachment welding failure.
COPY TO: |  | 1) DISPLAY IN UCB
2) GM/O&M
3) HOD (OS-BOILER)
(SIGNATURE OF BTF HEAD)
NAME:
DESIGNATION:
DATE: